## PIPEFLOW
R.C. COSTELLO & ASSOC., INC. -CONSULTING ENGINEERS- (310) 792-5870
Pressure Drop Calculations
Inputs
Nominal Pipe Diameter |  | 6 | inches | Inside Diameter |  | 6.357 | inches | 0.16147 | Nominal Pipe Diameter in meters D
Schedule |  | 10
Flow Rate |  | 15 | GPM | Click this Button |  |  |  | 0.00028315 | K/D
Viscosity |  | 1 | cps | to see a list of
Density |  | 8.455 | lbs/gal | acceptable pipe diameters
Absolute Roughness |  | 0.00015 | ft | and pipe schedules |  |  |  | 4.572e-05 | Absolute Roughness in meters K
Reynolds Number |  | Delta P Per 100ft. of pipe |  | Delta P Per 100ft. of pipe | [7 empty] | (7/RE)^0.9 |  | (0.27*I10)/I5
7554.7683 |  | 0.0010074 | psi | 0.00099829 | psi | [6 empty] | 0.0018629 |  | 7.6451e-05 |  | 6.2454
|  | 0.0022916 | feet | 0.0022709 | feet |  |  | A | 9.4504e+18
Linear Velocity |  | Friction Factor (Darcy) |  | Friction Factor (Darcy) |  |  |  | B | 137568387339.443
0.15144 | ft/sec | 0.033975 |  | 0.033669
|  | Churchill Equation |  | Chen Equation
|  | (1977) |  | (1979) |  |  |  | C | 0.0019647
INDEX | 2 |  | INDEX2
Nominal Pipe | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5s | 10s | 40s | 80s | xs | xxs
0.125 | no such Sch. | 0.307 | no such Sch. | no such Sch. | 0.269 | no such Sch. | 0.215 | no such Sch. | no such Sch. | no such Sch. |  | N/A | 0.307 | 0.269 | 0.215 | 0.215 | N/A
0.25 | no such Sch. | 0.41 | no such Sch. | no such Sch. | 0.364 | no such Sch. | 0.302 | no such Sch. | no such Sch. | no such Sch. |  | N/A | 0.41 | 0.364 | 0.302 | 0.302 | N/A
0.375 | no such Sch. | 0.545 | no such Sch. | no such Sch. | 0.493 | no such Sch. | 0.423 | no such Sch. | no such Sch. | no such Sch. |  | N/A | 0.545 | 0.493 | 0.423 | 0.423 | N/A
0.5 | 0.71 | 0.674 | no such Sch. | no such Sch. | 0.622 | no such Sch. | 0.546 | no such Sch. | no such Sch. | no such Sch. | 0.466 | 0.71 | 0.674 | 0.622 | 0.546 | 0.546 | 0.252
0.75 | 0.92 | 0.884 | no such Sch. | no such Sch. | 0.824 | no such Sch. | 0.742 | no such Sch. | no such Sch. | no such Sch. | 0.612 | 0.92 | 0.884 | 0.824 | 0.742 | 0.742 | 0.434
1 | 1.185 | 1.097 | no such Sch. | no such Sch. | 1.049 | no such Sch. | 0.957 | no such Sch. | no such Sch. | no such Sch. | 0.815 | 1.185 | 1.097 | 1.049 | 0.957 | 0.957 | 0.599
1.25 | 0.065 | 0.109 | no such Sch. | no such Sch. | 1.38 | no such Sch. | 1.278 | no such Sch. | no such Sch. | no such Sch. | 1.16 | 1.53 | 1.442 | 1.38 | 1.278 | 1.278 | 0.896
1.5 | 1.77 | 1.682 | no such Sch. | no such Sch. | 1.61 | no such Sch. | 1.5 | no such Sch. | no such Sch. | no such Sch. | 1.338 | 1.77 | 1.682 | 1.61 | 1.5 | 1.5 | 1.1
2 | 2.245 | 2.157 | no such Sch. | no such Sch. | 2.067 | no such Sch. | 1.939 | no such Sch. | no such Sch. | no such Sch. | 1.687 | 2.245 | 2.157 | 2.067 | 1.939 | 1.939 | 1.503
2.5 | 2.709 | 2.635 | no such Sch. | no such Sch. | 2.469 | no such Sch. | 2.323 | no such Sch. | no such Sch. | no such Sch. | 2.125 | 2.709 | 2.635 | 2.469 | 2.323 | 2.323 | 1.771
3 | 3.334 | 3.26 | no such Sch. | no such Sch. | 3.068 | no such Sch. | 2.9 | no such Sch. | no such Sch. | no such Sch. | 2.624 | 3.334 | 3.26 | 3.068 | 2.9 | 2.9 | 2.3
3.5 | 3.834 | 3.76 | no such Sch. | no such Sch. | 3.548 | no such Sch. | 3.364 | no such Sch. | no such Sch. | no such Sch. | no such Sch. | 3.834 | 3.76 | 3.548 | 3.364 | 3.364 | N/A
4 | 4.334 | 4.26 | no such Sch. | no such Sch. | 4.026 | no such Sch. | 3.826 | no such Sch. | 3.624 | no such Sch. | 3.428 | 4.334 | 4.26 | 4.026 | 3.826 | 3.826 | 3.152
5 | 5.345 | 5.295 | no such Sch. | no such Sch. | 5.047 | no such Sch. | 4.813 | no such Sch. | 4.563 | no such Sch. | 4.313 | 5.345 | 5.295 | 5.047 | 4.813 | 4.813 | 4.063
6 | 6.407 | 6.357 | no such Sch. | no such Sch. | 6.065 | no such Sch. | 5.761 | no such Sch. | 5.501 | no such Sch. | 5.187 | 6.407 | 6.357 | 6.065 | 5.761 | 5.761 | 4.897
8 | 8.407 | 8.329 | 8.125 | 8.071 | 7.981 | 7.813 | 7.625 | 7.437 | 7.187 | 7.001 | 6.813 | 8.407 | 8.329 | 7.981 | 7.625 | 7.625 | 6.875
10 | 10.482 | 10.42 | 10.25 | 10.136 | 10.02 | 9.75 | 9.562 | 9.312 | 9.062 | 8.75 | 8.5 | 10.482 | 10.42 | 10.02 | 9.75 | 9.75 | 8.75
12 | 12.438 | 12.39 | 12.25 | 12.09 | 11.938 | 11.626 | 11.374 | 11.062 | 10.75 | 10.5 | 10.126 | 12.438 | 12.39 | 12 | 11.75 | 11.75 | 10.75
Acceptable Pipe Schedules:
5 | 80 | 5 | S | XS | TYPE THESE IN
10 | 100 | 10 | S | XSS | AS A STRING I.E.
20 | 120 | 40 | S |  | '10S
30 | 140 | 80 | S
40 | 160
60
Acceptable Nominal Pipe Diameters in inches:
| 1/8 | 1-1/4 | 4
| 1/4 | 1-1/2 | 5 | To return to the input sheet
| 3/8 | 2 | 6 | click the input button
| 1/2 | 2-1/2 | 8 | below.
| 3/4 | 3 | 10
| 1 | 3-1/2 | 12
{goto}a200~ |  | \m
{BREAKOFF} |  | \0
/WGPE
{GOTO}preday~
{Wait @now+@time(0,0,8)}
{HOME}
{down}
{down}
* * * * * | * * * * * | * * * * * | * * * * * * | * * * * * | * * * * * | * * * * * * | * * * *
* | [6 empty] | *
* | [6 empty] | *
* |  | PIPEFLOW |  |  | VERSION 2.0 |  | *
* |  | 1993 & 1995 |  |  |  |  | *
* | [6 empty] | *
* |  | R.C.COSTELLO & ASSOC., INC. |  |  |  |  | *
* | [6 empty] | *
* |  | -CONSULTING ENGINEERS- |  |  |  |  | *
* | [6 empty] | *
* |  |  | (please wait) |  |  |  | *
* | [6 empty] | *
* | For best results set: | [5 empty] | *
* | Zoom Control to 84% |  | BY ROCKY C. COSTELLO |  |  |  | *
* | and have two (2) | [5 empty] | *
* | Toolbars Showing |  |  | November 15 , 1995 |  |  | *
* * * * * | * * * * * | * * * * * | * * * * * * | * * * * * | * * * * * | * * * * * * | * * * *
FRICTION FACTOR EQUATIONS
For information on the original Colebrook-White Equation
| Click Here |  |  |  |  | Pressure Drop
Equation
For information on the Churchill Equation
| Click Here |  |  |  |  | References
on equations
For information on the Chen Equation
| Click Here |  |  |  |  | Return to input page
Colebrook-White Equation
This is the original formula for calculating friction factor. It is implicit in friction
factor f , therefore it is not used. Friction factor (f) must be solved by trial and error.
In addition in the laminar flow regime, one must use f=64/Re, for Re < 2,100
See references for further detail.
Churchill Equation
This is a very good formula and in most cases agrees with the Chen equation.
In very low Reynolds numbers use this (i.e. transition and laminar ranges.)
This is a full regime equation.
Chen Equation
Considered the most accurate.
Use only in turbulent range.
Instructions
1. Input a nominal pipe diameter and a pipe schedule. The program automatically
looks up the correct I.D. in a table. For the (S) schedules type an apostrophe before
typing the schedule. For example '10s. All other schedules type in 40 or 80 etc.
2. Input flowrate of the fluid in GPM, density of the fluid in lbs/gallon and viscosity of the
fluid in centipoise.
3. For pipe roughness use .00015 ft.for commercial steel and stainless steel.
4. Program then calculates pressure drop in psi per 100 feet of pipe.
5. A word of caution. This program calculates pressure drop due to frictional losses
only. For difference in elevation use:
Delta P in psig=(H2-H1)*0.4331* specific gravity
Add this to the frictional loss.
Pressure Drop Equation
REFERENCES
1. Churchill, S.W. , Friction Factor Equation Spans All Fluid Flow Regimes, Chemical Engineering
Nov. 7, 1977, page 91.
2. Chen, N. H. , An Explicit Equation for Friction Factor in Pipe, Ind. Eng. Chem. Fund., 18, 296, 1979.
3. Gregory G.A. and Forgarasi M., Alternate to Standard Friction Factor Equation, Oil and Gas
Journal, April 1, 1985, page 120
4. Flow of Fluids, By Crane Technical Paper 410, 1979 edition
List
Input Input
Formulas
C-W
Input Input
Input Input
Churchill
Input Input
Chen
Input Input
Formulas
Formulas
Formulas
Instructions
Input Input
Input Input
Formulas
Delta P
References
Input Input
Formulas